Specification No. STN-1297/24-25

Amendment - I

| Sl. No. | As per specification | Existing | Amendment |
| --- | --- | --- | --- |
| 1. | SECTION III: Clause No. 45(b). Store Sample Testing : | ii. The test results will be binding on the suppliers and TGSPDCL in general will not allow any resampling. If the material fails in any of the tests carried out, the full lot of materials will be considered as rejected and if replacement is not possible due to consumption of the materials then in that case for whole of the rejected lot. | The test results will be binding on the suppliers and TGSPDCL in general will not allow any resampling. If the material fails in any of the tests carried out, the full lot of materials will be rejected and should be replaced. If materials are consumed due to emergency, the whole lot will be treated as rejected and it should be replaced at stores/site at supplier’s cost. |
| 2. | SECTION V : Clause No. 3. APPLICABLE STANDARDS: | Unless otherwise stipulated in this specification the following standards shall be applicable. i) IS:14255-1995 Aerial Bunched cable for working voltage up to and including 1100 Volts. ii) IS : 8130 – 1984 for Aluminium conductors for insulated electric cables (flexibility as per class II). iii) IS : 398 (Part-IV) 1994 : For all Aluminium Alloy Conductors (AAC) for overhead transmission purposes. | Unless otherwise stipulated in this specification the following standards shall be applicable. i) IS : 8130 – 1984 for Aluminium conductors for insulated electric cables (flexibility as per class II). ii) IS:14255-1995 Aerial Bunched cable for working voltage up to and including 1100 Volts. iii) IS : 398 (Part-IV) 1994 : For all Aluminium Alloy Conductors (AAC) for overhead transmission purposes. iv) XLPE Insulation properties as per a)EN 50397-1-2006 amended up-to-date b)Annexure - D of IS : 7098 (Part-3) 1993 or Annexure - F OF IEC 60502 (Pt-2) 2014 c) ASTM G 154 & IS : 10810 (Part-7) |
| 3. | SECTION V : Clause No.5 | 5.1(b) The Conductor (with protective barrier, wherever applied) shall be provided with cross linked polyethylene (XLPE) curing with Sioplus technology conforming to the standard Specification as per 14255/95 with latest amendment, | 5.1(b) A) The Conductor (with protective barrier, wherever applied) shall be provided with cross linked polyethylene (XLPE) Insulation properties as per i)EN 50397-1-2006 amended up-to-date ii)Annexure - D of IS : 7098 (Part-3) 1993 or Annexure - F OF IEC 60502 (Pt-2) 2014 iii) ASTM G 154 & IS : 10810 (Part-7) B) Filling (Water Blocking) : i) The stranded conductor shall be longitudinally water tight by means of water blocking material incorporated during the extrusion process. The use of grease/water swellable tape/water swellable powder etc is not permitted. ii) The water blocking material shall be stable at maximum operating conductor temperature of 90 Deg C. The water blocking compound shall be compatible with the conductor material. |

All other terms and conditions of the tender specification remains unaltered.

Sd/-

CHIEF ENGINEER/P&MM